SECTION 08376

“PARTHENON DOOR”
HOIST-UP FABRIC DOOR

PART 1   GENERAL

1.1	REFERANCES

The publications listed below form a part of this specification to the extent referenced.  The publications are referred to in the text by basic designation only.

1.	American Society for Testing and Materials (ASTM).

2.	National Electrical Manufacturer’s Association (NEMA).

3.	Underwriter’s Laboratories, Inc. (UL).

4.	American Institute of Steel Construction (AISC).

5.	American Iron and Steel Institute (AISI).

1.2	QUALITY ASSURANCE

A.	The material, construction, and operation of the door shall conform to the performance specifications contained herein.  Approved manufacturer is:

International Door, Inc., 8001 Ronda Drive, Canton,  MI 48187.

Telephone: 734-459-3000 Fax: 734-459-8962 or approved equal prior bid.

B.	Installation of the doors shall be by an authorized representative of the door manufacturer and shall be in accordance with approved shop drawings.  Mechanics shall be skilled and experienced in the erection of large hangar doors of the type specified herein.

1.3	DESIGN REQUIREMENTS

1.3.1	Door Design

Hangar doors shall be overhead hoist-up fabric type.   Doors shall be designed by a single manufacturer in accordance with the criteria specified herein.  Doors shall operate without binding, interference or damage to adjacent structure or weather-stripping.  Door components shall fit closely and be free from warping

08376-1

1.3.2  	Loading

Doors and swing-up mullions shall be designed as a unitary system to withstand wind pressure specified.  The deflection due to design wind load shall not exceed member length divided by 120 for steel and 30 for aluminum for any door member.  Fiber stresses due to combined dead load shall not exceed factors for the material being used and type of loading sustained.

1.3.3	Wind Loads

Components and cladding design pressures shall be considered for beam to fabric fastening.  Only bottom beams, intermediate beams, and swing-up mullions shall be considered as main resisting members.

1.3.4	Door Speed

Open and closing speeds shall be between 4.5” and 6.0” per second.

1.3.5	Door Support Loading

Installation shall allow for vertical variances in the hangar frame.  The contractor shall coordinate with the door manufacturer to ensure that doors have adequate adjustment ranges and can operate within predicted live load limits.

1.3.6	Door Plumbness

Collateral Steel shall meet vertical tolerances required for door plumb ness as specified by the door manufacturer.

1.4	SUBMITTALS

A. 	Submit detailed shop drawings of all work, and list the location in the building for each door.  Clearly show and describe in detail, detailed door assemblies, and adjacent construction, including elevations, sections, and details of door, track, hardware, and operating components, dimensions, finishes and relationship of door, frames, track, hardware and operating components to adjacent construction.

1.4.1	Samples

Submit color samples of panel fabric for approval.

1.4.2	Operating Drawings and Instructions

Furnish the following in duplicate at the completion of the installation.

08376-2

1.4.2.1	Assembly drawings and wiring schematics for doors.

1.4.2.2 Complete manufacturer’s manuals containing instructions for operation and maintenance of doors.

1.5	GUARANTEE

A.	Provide to the Owner a written guarantee, warranting the doors against any defects of materials and/or workmanship for the new door for a period of 1 year.  With proper maintenance, commencing from the date of final acceptance of the project.  Motors shall be guaranteed for a period of 1 year.  State that all door and control work that becomes defective during the guarantee period shall be repaired promptly, to the requirements of these Specifications and at no cost to the Owner.

1.6	DELIVERY AND STORAGE

Delivery of materials shall be in original rolls, packages, boxes, or crates bearing the manufacturers name, brand, model number, and installation location.  Store all materials in dry locations with adequate ventilation, free from dust and water, and available for inspection and handling.  Handle doors carefully to prevent damage.  Remove damaged items that cannot be restored to like-new condition and replace with new items.

PART 2 – PRODUCT

2.1	DOORS

2.1.1	Door Fabric

The fabric material shall be a one piece heavy duty vinyl coated fabric weighing approximately 19-22 ounces per square yard, capable of carrying 250 pounds per inch per panel.  It shall be UV stabilized, self extinguishing (0-75 flame spread), and suitable to withstand temperatures between + 158 to -38 degrees F.  The fabric shall be attached to both sides of the intermediate beams, top beam, and bottom beam with self tapping screws though corrosion resistant aluminum batten strips.  The fabric shall have been tested to meet the criteria of ASTM E-84-94 (flame spread – Class A interior wall and ceiling finish) and ASTM-D-1790 (cold cracking, brittleness and temperature).

2.1.2	Door Beams

The intermediate beams shall be corrosion resistant extruded aluminum, tempered after the extrusion process to ensure required strength and have a length to depth ratio not to exceed 100:1 to meet the required wind load.  Intermediate beams over 55’-0” long shall have a box type web to ensure torsional strength.  They shall be spaced 3-6 feet apart, dependent upon the wind load.  At each end of the beams there shall be a guide block of UHMW material, or rollers that run along the guides.

08376-3

2.1.3	Door Guides

The vertical guides shall be made of structural steel with a suitable depth and width dependent on the size of the intermediate beams.  The guides shall be designed to provide weather-sealing on the inside and the outside faces.  The guides shall be designed to provide sufficient strength to transfer the wind load and safety arrestor forces from the door beams, at maximum wind load, to the jamb steel support system.   The guides shall be easily replaceable in case of damage.  The installer shall furnish jamb structural steel fasteners of size and type required for attachment of the guide rails as shown on the approved shop drawings.

2.1.4	Belt/Cable System

A maximum of two belts/cables per door, running inside the door guides, shall be used to transmit motive force to the door unit.  Similarly, the quantity of sheaves used to guide the belts/cables shall be minimized to reduce maintenance requirements and spare parts inventories.  Belts/Cables shall be installed free of any kinks and the system design and sheave diameter shall be such to prevent the occurrence of any kinks or abnormal stress in the operating belts/cables.  Where belts/cables pass through openings in the structure the openings shall be constructed with UHMW material so as to prevent abrasion, wear, or damage to the belt/cables.  Sheave units shall be installed in accessible locations which allow inspection and preventive maintenance. Sheaves shall not be located in enclosed locations which are not readily accessible for visual inspection.

2.1.5	Drive Units

The door leaves shall have a UL/CSA labeled single or dual motor drive system with torque sized as appropriate for the weight of the door leaf.  The drive motors shall conform to NEMA MG 1, high-starting torque, reversible type, suitable for operation on 480-volt, 3 phase, 60 hertz current.  The gear motor shall be equipped with a drum on which the polyester belt of steel cables are wound.  If a single motor drive is used, the belt/cables shall be wound on the same drum.    The belts/cables shall be attached to the bottom beam via the safety arrestors.  A hand crank shall be supplied which fits on the motor for manual operation of the door in the event or a power failure.  The gear motor shall be removable without disturbing the limit switch adjustment.

2.1.6	 Safety Arrestors

Each door leaf shall be supplied with tow safety arrestors which activate and support the door in the event a belt or cable should break.  The moveable mullions, when provided, shall be provided with a lifting motor which has internal safety devices to prevent overload in case of obstruction as well as to prevent the mullion from falling in case of motor or primary break failure.

08376-4

2.1.7	Slack Belt/Cable Breaker

A safety device shall be used on all door leaf belts/cables which will sense a slack belt/cable condition and cut power to the appropriate drive unit to prevent an unsafe condition.

2.1.8	Bottom Beam

The bottom beam shall be designed with a suitable width and depth to carry the load of the intermediate beams when the door is open, and to ensure full closing and a tight floor seal in heavy winds.  A heavy U-Shaped bottom rubber seal shall be provided to form a tight seal with the floor even on uneven surfaces.

2.1.9	Wind Lock

Each door leaf shall be provided with two wind locks which activate and lock the bottom beam when the door reaches its closed position.  This locking action shall act to maintain a tight floor seal and intermediate beam stability even under conditions of heavy wind.

2.1.10	Swing-Up Mullion

The swing-up mullions, where indicated on the drawings, shall be designed to swing up under the door leaf in the raised position.  They shall be constructed of steel and coated with paint primer.  The mullion hinge pivot shall be of a maintenance free bearing design.  A mullion guide plate shall be provide for each mullion, welded to the mullion pit frame, and provided with corrosion resistant aluminum cover plates.  The mullion pit frame is to be provided under the Misc. Steel Section.  The electrical control panel shall provide and interlock function to coordinate door leaf and mullion operation to prevent equipment damage. Mullion push button for both up and down operation shall be of the constant pressure type.

2.1.11	Header Box

Header boxes, when provided, shall be constructed of carbon steel and factory primed with rust inhibitive paint.

2.1.12	Control Panel

The door manufacturer shall supply control panels for installation by the electrical subcontractor to operate the door units.  In multiple door system with swing up mullions, the control panel shall contain devices to control the sequence of door and mullion operation to insure safe operation.  The audible and visual warning devices (alarm bell and yellow rotating beacon) shall automatically signal for 5 seconds before any door section movement, remain continuously on while the door is in motion and reset immediately after movement stops.  The control panel shall also contain interlocks to

08376-5

preclude personnel injury, including an interlock between the power supply system and use of the hand crank for manual operation of the door unit.  The control panel and remote push button station shall be mounted a minimum of 48 inches above the floor.  The control equipment shall conform to NEMA ICS 2.  Enclosure shall conform to NEMA ICS 6, Type 12 (Industrial type).  Luminescent of reflective directional arrows shall be place adjacent to Luminescent or reflective directional arrows shall be place adjacent to the “Open and Close” buttons.  The Open and Stop controls shall be of the momentary contract type with seal-in contract.  The Close controls shall be of the constant pressure type.

2.1.13	Work of Other Trades

Refer to Section ELECTRICAL WORK, INTERIOR, for related work to install manufacturer furnished pre-wired control panels, including furnishing and installation of all wire, conduit, and accessories to connect all electrical door items in accordance with manufacturers  wiring diagram and National Electrical Code.  Electrical subcontractor to work with door installer during installation and testing operation of doors to correct any omission or incorrectly wired devices.  Refer to Section Bldg. Steel for preparation of building head, jamb, mullion wind bracing, and mullion pit steel for attachment of guide rails, header boxes, mullion lifting motors, and mullion pit steel.

2.3	OPERATION

2.3.1	Door Operation

The overhead “PARTHENON” hoist-up fabric door shall guide up and down in the weather sealing vertical guides attached to the structure.  The door shall operate by lifting the bottom beam upwards, thereby stacking the intermediate beams one on top of the other, with the fabric panel folding in pleats.  When the door is fully closed, the intermediate beams shall hang between the two fabric door panels thus pulling the fabric tight.  The tension created in the fabric panels shall stabilize the intermediate beams.  The safety arrestor shall be attached to each end of the bottom beam and shall travel in the vertical guide tracks.  The safety arrestors shall immediately stop the downward movement of the door in case of belt/cable failure.

2.3.2	Electrical Operation

When the door is completely opened it shall stop on the limit switch.  In case of over travel, a secondary limit switch shall cut off the drive unit’s motor current to prevent damage.  These two limit switched shall be activated by the uppermost intermediate beam.  The drive unit shall be stopped by the slack belt/cable breakers when the door is closed.  The slack breakers shall also stop the door in case of belt/cable rupture or if an obstruction should prevent the door from being closed.  The slack breakers shall be activated by weight or springs.  The control panel station and remote push button station

08376-6

located at the opposite side of the hangar shall be of the push button type.  The door operation shall be controlled by three buttons marked “Open,” “Closed,” and “Stop.”  They shall be controlled by momentary pressure to open and constant pressure to close.

Removing the pressure from the close button shall stop the motor drive and set the brake.  The mullion operation shall be controlled by two buttons marked “Horizontal Position” and “Vertical Position.”  Both buttons shall be controlled by constant pressure to open and to close.  Removing the pressure from either button shall stop the motor drive and set the brake.  The door manufacturer shall provide a NEMA enclosure which is factory wired and equipped with instantaneous overload relays.

2.3.3	Auxiliary Emergency Operation

The control panel shall be fed from an automatic transfer switch which will supply emergency power to the door systems in case of a power failure.  Provide a 120-volt terminal in the control panel that will be connected to the automatic transfer switch to signal the control panel when power has shifted to emergency operation.  The wiring from the control panel to the automatic transfer switch is by the Electrical Section.

2.4	PROTECTIVE COATINGS

After fabrication, metal surfaces shall be thoroughly cleaned of all mil scale, rust, oil, grease, and other foreign substances.  Rust preventative compound shall be applied to all steel machine finished parts immediately after cleaning.  Steel surfaces other than machine finished parts shall be coated with shop primer paint.  Paint shall be kept off of finished bearing surfaces.  Before assembly, surfaces that will be inaccessible after assembly shall be primed.  All match-marking shall be done on painted surfaces.

PART 3 EXECUTIONS

3.1	 EXAMINATION

Doors shall not be erected until the opening has been completed; the hangar roof has been completed and is under full dead load; and support steel for the door has been adjusted to the proper line, grade and elevation in accordance with the tolerances stated on the approved design drawings.  Any discrepancies in the prepared opening shall be brought to the attention of the Contracting Officer’s Representative and corrected before beginning door installation.  The structural steel erection subcontractor shall adjust the collateral steel for the door to the proper line, gage, and elevation in accordance with the approved tolerances on the drawings.

3.2	INSTALLATION

3.2.1	Assembly

Doors and accessories shall be assembled and installed in accordance with the approved

08376-7

shop drawings.  After installation is completed and before field painting is started, all abraded surfaces, field welds, and field bolts shall be thoroughly cleaned and coated with priming paint.  Field painting shall be specified in Section 09900 PAINTING, GENERAL.

3.2.2	Structural Steel

Preparation of building head and jamb steel for attachment of guide rails, header steel, and drive units shall be in accordance with Section Bldg. Steel.  Protection of dissimilar materials shall be in accordance with Section MISCELLANEOUS METALS.

3.2.3. Electrical

All conduits, wire, junction boxes, accessories, and all labor to wire and connect to and between all electrical equipment on or for the door shall be installed in accordance with the door manufacturer’s approved wiring diagrams and the Electrical Section of this specification.  The electrical control equipment will be furnished by the door manufacturer.  All conduits, wire, accessories, fused disconnect switches, and labor will be supplied by the Electrical Section.  The electrical wiring of the door shall be coordinated with the installer during installation in accordance with the control and power schematic wiring.

3.2.4	Building Power

If permanent electrical power is not available when the door is being installed, the General Contractor under Temporary Electric Power, shall make provision for and obtain a temporary source of electrical power to allow the door manufacturer to install, test, and adjust the door under power.

3.3	ADJUSTING

Immediately after door installation is complete, the door manufacturer’s technical representative shall perform a complete operating test in the presence of the Contracting Officer’s Representative.  Defects disclosed by the test shall be corrected.  Doors shall be retested and adjusted until the entire installation is fully operable and acceptable.

3.4	CLEANING

Upon completion of installation, all doors, and frame surfaces shall be cleaned in accordance with the manufacturer’s recommended procedures.  Abrasive, caustic, or acid cleaning agents which may damage vinyl fabric shall not be used.

08376-8

3.5	PROTECTION

Doors shall be protected from damage and contamination by other materials such as paint.  Prior to completion and acceptance of work, damaged fabric, batten bars, or other material shall be restored to original condition or replaced with new materials.

3.6	TURNOVER

A.	A door fabric patch kit shall be supplied with approximately 30 square feet of fabric and all other material required for door panel repair.

B.	A training session shall be provided for the door operating personnel and maintenance department.  The training shall outline door operation, troubleshooting, and repair guidelines.

END OF SECTION 08376

08376-9